Guide Specification - SECTION 08 51 13  ALUMINUM WINDOWS

WAUSAU 2500 S.E.A.L.™ SERIES  Interior ICU Observation Windows

[NOTE: Instructional and advisory language in grey italic font.]

PART 1 GENERAL

  - SUMMARY

- Section Includes:

  - All interior ICU observation windows furnished and installed as shown on drawings, specified in this section.

  - All labor, materials, tools, equipment and services needed to furnish and install ICU observation windows for sound, energy, air and/or light control.

  - Components furnished with installed interior windows.

  - Installation accessories furnished and installed.

  - REFERENCE

- Refer to AAMA/WDMA/CSA 101/I.S.2/A440 for a complete list of references and industry standards.

1.03 SYSTEM DESCRIPTION AND PERFORMANCE REQUIREMENTS

A. 	Design Loads - Allowable Stress Design (ASD)

  - The design internal pressure for interior windows will be:  (Specify ±10 psf minimum internal pressure)

    - ___ psf positive and negative

[NOTE: Determination of Design Load(s) is the sole responsibility of the building's Engineer of Record, considering factors not included in Contract Documents, such as code interpretation issues or prescriptive requirements.  WAUSAU is not responsible for determining Design Loads and strongly recommends that ASD Design Loads (in psf or Pa) specific to all relevant areas of the building be provided by the Specifier.]

b. All structural components, including framing members, hardware, and anchors shall be designed accordingly.

- Sustainable Design Requirements

  - The products provided under this section may affect LEED® certification for the project.  Provide documentation in accordance with the applicable version USGBC’s “LEED® for New Construction and Major Renovation,” verifying that the components, processes and/or assemblies specified herein conform to the following requirements.  (Select only those Credits needed for the level of certification sought. Modify criteria as necessary for other LEED® programs or versions applicable to specific projects.)

    - MR  Recycled Content

      - Provide window assemblies (aluminum framing, glass and other components) containing no less than ___% (Specify up to 15%) combined recycled content by assembly weight.

      - Combined content to be calculated as post-consumer plus one-half pre-consumer recycled content by weight.

      - Report pre- and post-consumer recycled content separately.

      - All recycled secondary aluminum billet must meet Aluminum Association content requirements for the alloy used.

[NOTE: Secondary aluminum billet contains a high percentage of pre-consumer recycled content, however, glass comprises the majority of the weight of a glazed window assembly.]

    - EQ  Low-Emitting Materials – Adhesives and Sealants

      - All interior primers, structural glazing adhesives and metal-to-metal sealants used on site must meet applicable South Coast Air Quality Management District (SCAQMD) Rule #1168 VOC limits.

    - EQ  Controllability of Systems

      - Provide blinds in viewing windows with occupant-enabled hardware.

      - Window sizes and configurations as shown on drawings.

  - SUBMITTALS

- General Requirements

  - Provide all submittals in a timely manner to meet the required construction completion schedule.

- Shop Drawings

  - Shop drawings must be prepared wholly by the window manufacturer, or a qualified engineering services firm under the guidance of the manufacturer.  Shop drawings for pre-engineered configurations may be prepared by installers upon written manufacturer consent.

  - Provide design details along with bid proposals to define system aesthetic and functional characteristics.

  - Provide up to three photocopied sets of shop drawings, including half size details of all necessary conditions.

- Samples

  - Components:  Submit samples of anchors, fasteners, hardware, assembled corner sections and other materials and components as requested by Architect.

  - Finish:  Submit color samples for Architect's approval as requested.

  - QUALITY ASSURANCE

- Qualifications:  Upon request, the window manufacturer shall provide written consent for installation subcontractor to install window products to be used on this project.

  - DELIVERY, STORAGE AND HANDLING

- Packing, Shipping, Handling and Unloading

  - Materials will be packed, loaded, shipped, unloaded, stored and protected in accordance with AAMA CW-10.

  - WARRANTY

- Aluminum Window Warranty

  - Products:  Submit a written warranty, executed by the window manufacturer, for a period of ___ (up to 10) years from the date of manufacture, against defective materials or workmanship, including substantial non-compliance with applicable specification requirements and industry standards, which result in premature failure of the windows, finish, factory-glazed glass, or parts, outside of normal wear.

  - In the event that windows or components are found defective, manufacturer will repair or provide replacement material without charge at manufacturer’s option.

  - Warranty for all components must be direct from the manufacturer (non pass-through) and non pro-rated for the entire term.  Warranty must be assignable to the non-residential owner, and transferable to subsequent owners through its length.

PART 2 PRODUCTS

2.01 MANUFACTURERS

- Acceptable Manufacturer

  - Drawings and specification are based on:

    - Wausau Window and Wall Systems - 2500 S.E.A.L. Series Interior ICU Windows.

    - Base bid will be Wausau Window and Wall Systems.

  - Substitutions

    - Other manufacturers’ products that meet or exceed specified design requirements may be considered.  Submit the following information with request for substitutions at least ten (10) working days prior to bid date.

      - Test reports specified in 1.03.

      - Full proposal details and samples specified in 1.04.

      - Copy of manufacturer's warranty specified in 1.07.

      - Proof of at least 10 years experience in the design and fabrication of interior prime windows with between-glass blinds.

      - Other information as requested for evaluation

  - Substitute products not pre-approved by the Architect via addenda will not be considered.

  - Clear preference will be given to products produced in LEED®-certified manufacturing  facilities.

2.02 MATERIALS

- Aluminum Framing Members

  - Extruded aluminum billet, 6063-T6 alloy for primary non-radius components; 6063-T6 or 6061-T6 for anchor components; all meeting the requirements of ASTM B221.

  - Aluminum sheet alloy 5005-H32 (for anodic finishing), or alloy 3003-H14 (for painted or unfinished sheet) meeting the requirements of ASTM B209.

  - Principal window frame and access panel members will be a minimum 0.093" in thickness at glazing legs, hardware mounting webs and section flanges.

  - Extruded or formed trim components will be a minimum 0.060" in thickness.

  - Frame depth 2 ½ " minimum.

  - Access panel sections must close flush with adjoining frame surfaces at operable side.

    - Overlap access panels will not be accepted.

2.03 COMPONENTS

- Hardware (Select from options as noted)

  - All steel components including attachment fasteners to be 300 Series stainless steel except as noted.

  - Extruded aluminum components 6063-T6.

  - Locking handles, bases and strikes to be die cast, white bronze or stainless steel in manufacturer’s standard surface finish.

  - Thermo-plastic or thermo-set plastic caps, housings and other components to be injection-molded nylon, extruded PVC, or other suitable compound.

  - Hardware to be custodial-operated and include: (Select from appropriate options listed in the WAUSAU Hardware Selection Guide: concealed hinge pins and blocks, concealed locks, retainer clips, lift blocks.)

- Sealants

  - All sealants shall comply with applicable provisions of AAMA 800 and/or Federal Specifications FS-TT-001 and 002 Series.

  - Frame joinery sealants shall be suitable for application specified and as tested and approved by window manufacturer.

- Glass

  - Provide in accordance with Section 08 80 00.

- Glazing

  - Provide in general accordance with Section 08 80 00.

  - Glazing method shall be in general accordance with the GANA Glazing Manual for specified glass type, or as approved by the glass fabricator.

- Glazing Materials

  - Setting Blocks/Edge Blocking:  Provide in sizes and locations recommended by GANA Glazing Manual. Setting blocks used in conjunction with soft-coat low-e glass shall be silicone.

  - Back-bedding tapes, expanded cellular glazing tapes, toe beads, heel beads and cap beads shall meet the requirements of applicable specifications cited in AAMA 800.

  - Glazing gaskets shall be non-shrinking, weather-resistant, and compatible with all materials in contact.

  - Structural silicone sealant where used shall meet the requirements of ASTM C1184.

  - Spacer tape in continuous contact with structural silicone shall be tested for compatibility and approved by the sealant manufacturer for the intended application.

  - Gaskets in continuous contact with structural silicone shall be extruded silicone or compatible material.

- Glazed Access Panel:

  - Hinged (lift-off) access panel (Select one)  provided with Allen locks for custodial operation.

  - Finish to match window frames.

- Integral Venetian Blinds:

  - 5/8" or 1" (Select one)  wide aluminum slat blinds. Blind color shall be _____________.  (Specify from standard color chart.)

  - Blind to be integrally mounted between the dual glazing.

  - Tilt-control knob will be located on the operable face and incorporate a "slip clutch" feature.

  - Raise and lower pull cords will be located between glass for access only when glazed access panel is opened.

2.04 FABRICATION

- General:

  - Finish, fabricate and shop assemble frame and access panel members into complete windows under the responsibility of one manufacturer.

- Frames and Access Panels:

  - Miter and weld each corner.

- Hardware:

  - Concealed Hinges

    - Provide two die cast concealed hinge pins, retained in injection molded nylon hinge blocks at sill and spring steel hinge clips at head.

  - Locks

    - Die cast or stainless steel Allen-keyed locks for custodial operation shall secure panel in closed position. (Refer to WAUSAU Hardware Selection Guide for other options.)

    - Provide locks at maximum 40" spacing.

- Weather-stripping:

  - Bulb- or fin-type neoprene, EPDM, dual-durometer PVC, polypropylene, TPE, or other suitable material as approved by the window manufacturer.

  - Miter, crowd, stake or join at corners.

2.05 FINISHES

- Finish of Aluminum Components

  - Finish of all exposed areas of aluminum windows and components shall be done in accord with the appropriate AAMA Voluntary Guide Specification shown (Select from below).

Designation			Description			Standard 				Color

AAM10C21A41			Clear Class I 			AAMA 611				Clear

Eco-friendly etch

AAM10C21A44			Electrolytically			AAMA 611				Champagne, Light Bronze, Medium Bronze

Deposited Class I								Dark Bronze, Extra Dark Bronze, Black					Eco-friendly etch

Organic Paint			50% PVDF,				AAMA 2603				____________ (As selected by Architect)

Enamel, Acrylic									Suitable for INTERIOR finishes

or Polyester

[NOTE: For detailed specifications of other surface treatments and finishes available, as well as sustainable finishing process specification upgrades contact Linetec or Wausau Window and Wall Systems. Color selection is recommended, for the most competitive bids.]

PART 3 EXECUTION

3.01 EXAMINATION

- Site Verification of Conditions

  - Verify that building substrates permit installation of windows according to the manufacturer's instructions, approved shop drawings, and contract documents.

  - Do not install windows until unsatisfactory conditions are corrected.

3.02 INSTALLATION

- Erection of Aluminum Windows

  - Install windows with skilled workers in accordance with approved shop drawings, installation instructions, specifications, and the AAMA Commercial Window and Door Installation Manual.

  - Windows must be installed plumb, square and level for proper operation.

  - Aluminum that is not organically coated shall be insulated from direct contact with steel, masonry, concrete or other dissimilar metals by bituminous paint, rust-inhibiting primer, non-conductive shims or other suitable insulating material, if exposure to moisture will occur at any point during construction or occupancy.

[DISCLAIMER:  Wausau Window and Wall Systems takes no responsibility for product selection or application, including, but not limited to, compliance with building codes, safety codes, laws, merchantability or fitness for a particular purpose; and further disclaims all liability for the use, in whole or in part, of these Guide Specifications in preparation of project specifications and/or other documents.  Guide Specifications are subject to change at any time, without notice, and at Wausau’s sole discretion.]

“S.E.A.L.” is a trademark of Apogee Wausau Group.  All rights reserved.  ©2014 Apogee Wausau Group, Inc.