Guide Specification - SECTION 08 51 13   ALUMINUM WINDOWS

WAUSAU 3151-SHT and 3150-DHT SERIES  Tilt Sash Hung and Fixed

[NOTE: Instructional and advisory language in grey italic font.]

PART 1 GENERAL

  - SUMMARY

- Section Includes:

  - All exterior Architectural Performance Class (AW) windows furnished and installed as shown on drawings, specified in this section and designated in AAMA/WDMA 101/I.S.2-97.

  - All labor, materials, tools, equipment and services needed to furnish and install AW Class windows.

  - Components furnished with installed windows.

  - Installation accessories furnished and installed.

  - REFERENCES

- Refer to AAMA/WDMA 101/I.S.2-97 for a complete list of references and industry standards.

1.03 SYSTEM DESCRIPTION AND PERFORMANCE REQUIREMENTS

[IMPORTANT DISCLAIMER: Wausau 3151-SHT and 3100-DHT Series windows have not been tested to current industry standards, therefore references contained herein should be considered out of date. Any updated testing deemed necessary will only be done on project-specific basis at others’ expense.  Wausau takes no responsibility for testing cost, or for product performance other than as listed herein.]

A. 	 Design Wind Loads - Allowable Stress Design (ASD)

  - The design wind pressure for the project will be:  (Specify)

    - ___ psf positive and negative; ___ psf negative at corner zones

    - Per wind pressure diagram, (or)

    - Per local building codes

[NOTE: Determination of Design Load(s) is the sole responsibility of the building's Engineer of Record, considering Code interpretation issues and/or prescriptive requirements not included in Contract Documents.  WAUSAU is not responsible for determining Design Loads and strongly recommends that ASD Design Loads (in psf or Pa) specific to all relevant areas of the building be provided by the Specifier.]

  - All structural components, including meeting rails, mullions and anchors shall be designed accordingly, complying with deflection and stress requirements of Paragraph 1.03.B.

- Air, Water and Structural Performance Requirements

  - When tested in accordance with cited test procedures, windows shall meet or exceed the following performance criteria, as well as those indicated in AAMA/WDMA 101/I.S.2-97 for Architectural AW Performance Class windows, Performance Grade 70 (AW70) unless otherwise noted herein.

    - Test units shall not be smaller in either width or height than the “Gateway Test Size” specified in AAMA/WDMA 101/I.S.2-97 for AW Performance Class.

    - “Downsize” testing to meet Optional Performance Class requirements specified herein shall not be permitted.

    - Test units shall employ manufacturer’s standard sealing, lock spacing and anchorage.

  - Air Test Performance Requirements

    - Air infiltration maximum 0.3 cfm per square foot at 6.24 psf pressure differential when tested in accord with ASTM E283.

  - Water Test Performance Requirements

    - No uncontrolled water leakage at 12.00 psf static pressure differential, with water application rate of 5 gallons/hr/sq ft when tested in accord with ASTM E331.  Static water test shall be repeated after application of design test pressures.

  - Structural Test Performance Requirements

    - Uniform Load Deflection Test

      - No deflection of any unsupported span L of test unit (framing rails, muntins, mullions, etc.) in excess of L/175 at both a positive and negative load of 70 psf (design test pressure) when tested in accord with ASTM E330.

    - Uniform Load Structural Test

      - Unit to be tested at 1.5 x design test pressure, both positive and negative, acting normal to plane of wall in accord with ASTM E330.

      - No glass breakage; permanent damage to fasteners, hardware parts, or anchors; damage to make windows inoperable; or permanent deformation of any main frame or ventilator member in excess of 0.2% of its clear span.

- Life Cycle Testing

  - When tested in accordance with AAMA 910-93, there is to be no damage to fasteners, hardware parts, support arms, activating mechanisms or any other damage that would cause the window to be inoperable at the conclusion of testing.

    - Air infiltration and water resistance tests shall meet the primary performance requirements specified after completion of 2500 operational cycles and misuse testing.

- Condensation Resistance and Thermal Transmittance Performance Requirements

(Wausau recommends specifying U-Factor and SHGC requirements by citing the values used in the default, prescriptive or performance compliance path option employed during permitting. Performance of specific frame-glass combinations in this Wausau product family can be obtained from the NFRC Certified Products Directory, an NFRC CMA Bid Certificate, or an AAMA 507 report. Coordinate with 08 80 00 Glazing.)

  - Perform thermal tests in accordance with NFRC 102 and/or AAMA 1503, or provide finite element computer thermal modeling and calculations per NFRC 100, NFRC 705 or AAMA 507, using DOE/LBL THERM, WINDOW, and/or CMAST software.

    - Thermal Transmittance (U-Factor) for the overall window area shall be less than or equal to _____ BTU/hr-ft2-(F.

    - Solar Heat Gain Coefficient (SHGC) for the overall window area shall not exceed ____.

    - Condensation Resistance Factor (CRF) requirements:  CRF minimum ___ (Frame) and CRF minimum ___ (Glass).

(Visit www.aamanet.org to access the AAMA online CRF Selection Tool. CRF varies with configuration, frame depth, and glass type.  Contact WAUSAU for CRF test data on specific frame-glass combinations in this product family.)

[DISCLAIMER:  Condensation on interior surfaces of installed windows may be affected by many variables, including, but not limited to, component thermal performance, thermal mass of surrounding materials, interior trim coverage and air flow conditions, weather and mechanical system design.  Since many of these variables are outside of our control, WAUSAU makes no representations or warranties against the formation of condensation. Testing is conducted on pre-defined configurations under controlled and steady-state laboratory conditions, as specified above.]

- Acoustic Performance Requirements

  - Perform acoustical tests in accordance with ASTM E90 and ASTM E1425 on the glass type(s) specified in 08 80 00, rigidly supported in aluminum framing of the same product type.

  - “Glass-only” test results shall not be acceptable.

  - Sound Transmission Class (STC) shall not be less than ___. (Specify STC 31 for 1” insulating glass with makeup of ¼” glass – ½” air space – ¼” glass. Coordinate with 08 80 00 Glazing.)

  - Outdoor-Indoor Transmission Class (OITC) shall not be less than  ____. (Specify OITC 25 for 1” insulating glass with makeup of ¼” glass – ½” air space – ¼” glass. Coordinate with 08 80 00 Glazing.)

- Sustainable Design Requirements

  - The products provided under this section may affect LEED® certification for the project.  Provide documentation in accordance with the applicable version of USGBC’s “LEED® for New Construction and Major Renovation,” verifying that the components, processes and/or assemblies specified herein conform to the following requirements.  (Select only those Credits needed for the level of certification sought. Modify criteria as necessary for other LEED® programs or versions applicable to specific projects.)

    - EA  Optimize Energy Performance

      - Area-weighted overall U-Factor not to exceed that specified in 1.03.

      - Area-weighted center-of-glass or overall SHGC less than or equal to that specified in 1.03.

    - EA  On-Site Renewable Energy

      - Design framing to accept façade-integrated PV modules and associated NEC-compliant wiring where shown on drawings.

      - Obtain UL 1703 listing for laminate support.

    - MR  Recycled Content

      - Provide window assemblies (aluminum framing, glass and other components) containing no less than ___% (Specify up to 15%) combined recycled content by assembly weight.

      - Combined content to be calculated as post-consumer plus one-half pre-consumer recycled content by weight.

      - Report pre- and post-consumer recycled content separately.

      - All recycled secondary aluminum billet must meet Aluminum Association content requirements for the alloy used.

[NOTE: Secondary aluminum billet contains a high percentage of pre-consumer recycled content, however, glass comprises the majority of the weight of a glazed window assembly.]

    - EQ  Increased Ventilation

      - Provide operable windows with occupant-enabled hardware.

      - Window sizes and configurations as shown on drawings.

    - EQ  Low-Emitting Materials – Adhesives and Sealants

      - All interior primers, structural glazing adhesives and metal-to-metal sealants used on site must meet applicable South Coast Air Quality Management District (SCAQMD) Rule #1168 VOC limits.

    - EQ  Controllability of Systems

      - Provide operable windows with occupant-enabled hardware.

      - Window sizes and configurations as shown on drawings.

    - EQ  Thermal Comfort- Design

      - Provide thermal barrier framing and insulating glass edge construction as specified herein and in 08 80 00 Glazing.

    - EQ  Daylight and Views

      - Area-weighted overall VT not less than 0.____ (Specify – Coordinate with 08 80 00 Glazing) per NFRC 200.

      - Window sizes and configurations as shown on drawings.

  - SUBMITTALS

- General Requirements

  - Provide all submittals in a timely manner to meet the required construction completion schedule.

- Shop Drawings

  - Shop drawings must be prepared wholly by the window manufacturer, or a qualified engineering services firm under the guidance of the manufacturer.  Shop drawings for pre-engineered configurations may be prepared by installers upon written manufacturer consent.

  - Provide design details along with bid proposals to define system aesthetic and functional characteristics.

  - Provide up to three photocopied sets of shop drawings, including half size details of all necessary conditions.

- Samples

  - Components:  Submit samples of anchors, fasteners, hardware, assembled corner sections and other materials and components as requested by Architect.

  - Finish:  Submit color samples for Architect's approval as requested.

- Test Reports and Calculations

(Specifier Note: Wausau 3150-DHT and 3151-SHT tilt sash hung windows have not been tested to current industry standards.)

  - Submit certified independent laboratory test reports verifying compliance with all test requirements of 1.03.

  - Submit structural calculations indicating adequacy of all materials furnished under this section, to meet the uniform and structural load requirements as specified in 1.03.

  - QUALITY ASSURANCE

- Qualifications:  Upon request, the window manufacturer shall provide written consent for the installation subcontractor to install window products to be used on this project.

- In-Plant Testing:  Conduct detailed quality audits and ASTM E331 static water infiltration testing on a minimum of 4% of factory-glazed windows prior to shipping, subject to reasonable unit size restrictions.

  - Each tested unit shall be identified with a removable sticker on the inside glass face.

  - Provide detailed documentation of in-plant testing upon request.

  - DELIVERY, STORAGE AND HANDLING

- Packing, Shipping, Handling and Unloading

  - Materials will be packed, loaded, shipped, unloaded, stored and protected in accordance with AAMA CW-10.

  - WARRANTY

- Aluminum Window Warranty

  - Products:  Submit a written warranty, executed by the window manufacturer, for a period of ___ (up to 10) years from the date of manufacture, against defective materials or workmanship, including substantial non-compliance with applicable specification requirements and industry standards, which result in premature failure of the windows, finish, factory-glazed glass, or parts, outside of normal wear.

[NOTE: Refer to the WAUSAU Standard Limited Warranty for detailed exclusions, qualifications and limitations. Screens and balances are warranted for one year.]

  - In the event that windows or components are found defective, manufacturer will repair or provide replacement material without charge at manufacturer’s option.

  - Warranty for all components must be direct from the manufacturer (non pass-through) and non pro-rated for the entire term.  Warranty must be assignable to the non-residential owner, and transferable to subsequent owners through its length.

PART 2 PRODUCTS

2.01 MANUFACTURERS

- Acceptable Manufacturer

  - Drawings and specification are based on:

    - Wausau Window and Wall Systems – (Select one or both) 3150-DH Series Tilt Sash Double-Hung (and/or 3151-DH Series Tilt Sash Single-Hung) and Fixed Windows.

    - Base bid will be Wausau Window and Wall Systems.

  - Substitutions

    - Other manufacturers’ products that meet or exceed specified design requirements may be considered.  Submit the following information with request for substitutions at least ten (10) working days prior to bid date.

      - Test reports specified in 1.03.

      - Full proposal details and samples specified in 1.04.

      - Copy of manufacturer's warranty specified in 1.07.

      - Proof of at least 10 years experience in the design and fabrication of AW Performance Class windows.

      - Other information as requested for evaluation

  - Substitute products not pre-approved by the Architect via addenda will not be considered.

  - Clear preference will be given to products produced in LEED®-certified manufacturing  facilities.

2.02 MATERIALS

- Aluminum Framing Members

  - Extruded aluminum billet, 6063-T5 or T6 alloy for primary non-radius components; 6063-T5 or T6, 6005-T5, 6105-T5 or 6061-T6 for anchor components; all meeting the requirements of ASTM B221.

  - Aluminum sheet alloy 5005-H32 (for anodic finishing), or alloy 3003-H14 (for painted or unfinished sheet) meeting the requirements of ASTM B209.

  - Principal window frame members will be a minimum 0.060" in thickness except at frame sills, which will be 0.093” minimum thickness.

  - Extruded or formed trim components will be a minimum 0.060" in thickness.

  - Frame depth 4 ½ " minimum.

  - Sills shall be sloped. Sill must allow for drainage to the exterior.

  - Frame-to-sash interface shall be designed for sweep seals, to prevent loss of weather-strip contact under positive pressure.

  - Sash must be tubular, tilt to the interior for cleaning, and be removable to the interior for maintenance.

  - Frames to be designed for self-mulling (stacking), as well as incorporation of integral single-frame transom and spandrel lites.

  - Screen frame must not protrude from exterior of window frame.

2.03 COMPONENTS

- Hardware (Select from options as noted)

  - All attachment fasteners to be 300 Series stainless steel.

    - Other steel components shall be protected by corrosion resistant coatings meeting the requirements of AAMA 907.

  - Extruded aluminum components 6063-T5 or -T6.

  - Locking handles, bases and strikes to be die cast, white bronze, aluminum, or stainless steel in manufacturer’s standard surface finish.

  - Thermo-plastic or thermo-set plastic caps, housings and other components to be injection-molded nylon, extruded PVC, or other suitable compound.

  - Hardware to be (Select one) occupant-operated (or custodial-operated) and include: (Select from appropriate options listed in the WAUSAU Hardware Selection Guide: block-and-tackle balances, UltraliftTM balances, sweep latches, keyed sweep latches, tilt release slide bars, head/sill spring latches, limit stops, tamper-resistant limit stops.)

- Sealants

  - All sealants shall comply with applicable provisions of AAMA 800 and/or Federal Specifications FS-TT-001 and 002 Series.

  - Frame joinery sealants shall be suitable for application specified and as tested and approved by window manufacturer.

- Glass

  - Provide in accordance with Section 08 80 00.

  - Sealed insulated glass shall be tested and certified in accord with ASTM E2190.

- Glazing

  - Provide in general accordance with Section 08 80 00.

  - Glazing method shall be in general accordance with the GANA Glazing Manual for specified glass type, or as approved by the glass fabricator.

  - Only bead glazing is acceptable, allowing for glass replacement without removal of operating sash.

- Glazing Materials

  - Setting Blocks/Edge Blocking:  Provide in sizes and locations recommended by GANA Glazing Manual. Setting blocks used in conjunction with soft-coat low-e glass shall be silicone.

  - Back-bedding tapes, expanded cellular glazing tapes, toe beads, heel beads and cap beads shall meet the requirements of applicable specifications cited in AAMA 800.

  - Glazing gaskets shall be non-shrinking, weather-resistant, and compatible with all materials in contact.

  - Structural silicone sealant where used shall meet the requirements of ASTM C1184.

  - Spacer tape in continuous contact with structural silicone shall be tested for compatibility and approved by the sealant manufacturer for the intended application.

  - Gaskets in continuous contact with structural silicone shall be extruded silicone or compatible material.

- Steel Components

  - Provide steel reinforcements as necessary to meet the performance requirements of 1.03.

  - Concealed steel anchors and reinforcing shall be factory painted after fabrication with TGIC powder coating, or rust-inhibitive primer complying with Federal Specification TT-P-645B.

- Muntins: (Optional)

  - Provide muntin grids as shown on architectural drawings.

  - Finish to match window frames.

- Panning: (Optional)

  - Provide extruded aluminum panning to receive replacement windows as shown on architectural drawings.

  - Panning shall be pre-assembled and all joinery back sealed prior to installation.

  - Finish to match window frames.

- Receptors:  (Optional)

  - Provide extruded aluminum receptors to receive windows, as shown on architectural drawings.

  - Finish to match window frames.

- Insect Screens: (Optional: Specify full screens or half screens for 3150-DHT double-hung; half screens for 3151-DHT single hung.)

  - Provide half screens at exterior of lower sash.

  - Tubular extruded aluminum frames shall meet the requirements of ANSI/SMA 1004.

  - Screen frame finish to match window frames.

  - Aluminum cloth shall comply with GSA-FS-RR-W-365 and USDC-CS-138 with 18 x 16 mesh.

  - Cloth mesh color shall be ________________. (Specify bright mesh or charcoal mesh)

- Dual Glazed Access Panel: (Optional)

  - Hinged (lift-off) access panel (Select one) will be constructed with mitered corners, mechanically staked over a solid aluminum corner block leaving hairline joinery.

  - Finish to match window frames.

  - Provide Allen locks for custodial operation.

  - Latches must be removable as necessary for access door operation.

- Integral Venetian Blinds: (Optional)

  - 5/8" wide aluminum slat blinds. Blind color shall be ______.

  - Blind to be integrally mounted between the dual glazing.

  - Flush tilt-control housing with removable control knob will be located on the interior face and incorporate a "slip clutch" feature.  Raise and lower pull cords will be located between glass for access only when access ventilator is opened.

2.04 FABRICATION

- General:

  - Finish, fabricate and shop assemble frame and sash members into complete windows under the responsibility of one manufacturer.

  - No bolts, screws or fastenings shall impair independent frame movement, or bridge the thermal barrier, unless such bridging was also present in thermal test units and thermal models.

  - Fabricate to allow for thermal movement of materials when subjected to a temperature differential from -30 (F to +180 (F.

- Frames:

  - Cope and mechanically fasten each corner, or miter and weld each corner; then seal weather tight.

  - Make provisions for continuity of frame joinery seals at extrusion webs.

- Main Sash

  - Miter all corners and mechanically stake over a solid extruded aluminum corner block, set and sealed in epoxy, leaving hairline joinery, then sealed weather tight.

  - Make provisions for continuity of sash ventilator joinery seals at extrusion webs.

- Glass Drainage: (field glazed units only)

  - Provision shall be made to insure that water will not accumulate and remain in contact with the perimeter area of sealed insulated glass.

- Hardware: (Select from options as noted.)

  - Balances:

    - Balances must provide a positive lifting force through the full range of sash travel.  Sash travel may be limited on oversize units.

    - When properly adjusted, balances must hold the sash stationary at any open position.

    - Balance shoes must lock tilt pins when in the normal operating position, and engage frames to prevent sash movement when in the tilted position.

    - Ultra-liftTM balances standard for improved manual assist ratio. (Block-and-tackle type balances optional.)

  - Locks:

    - Die cast zinc sweep lock; one per meeting rail.

    - Provide stainless steel or die cast strikes.

    - Finish to be flat black. (Optional white bronze.)

  - Lift Handles:

    - Provide two removable die cast lift handles on lower sash.

    - Recessed glazing beads shall serve as secondary lift handles on upper and lower sashes.

  - Tilt Release Slide Bars:

    - Provide two black nylon tilt release slide bars at the top stile of each sash, secured by Allen head cap screws for custodial operation only.

    - Heads of retainer screws shall be positively secured when the slide bar is in the locked position.

  - Hardware Options: (Select appropriate combination from WAUSAU Hardware Selection Guide.)

    - Provide Allen lock-released sweep latches. (Optional)

    - Automatic spring-loaded head and/or sill locks shall secure sash in closed position. (Optional)

    - Provide jamb-mounted limit stops. (Optional)

- Thermal Break Construction

  - Frame and sash members must include a thermal break applied in the manufacturer's facility, using concealed low conductance poured-in-place polyurethane in a pre-treated cavity.

  - After proper curing, the aluminum bridge section must be removed to provide a 1/4" separation between exterior and interior metal surfaces.

  - Quality assurance records must be maintained and available as requested.

  - Black extruded PVC shall shield any member exposed to both interior and exterior.

- Weather-stripping:

  - Provide two rows of "silicoated" woven pile weather-strip with MylarTM side or center fins at both sash center weathering seals and outer seals.

  - Provide factory-installed patch pile to maintain seal continuity at interlock ends.

  - Bed lower sash in a fin-type neoprene, EPDM or PVC weather-strip at the sash/frame water shed.

2.05 FINISHES

- Finish of Aluminum Components

  - Finish of all exposed areas of aluminum windows and components shall be done in accord with the appropriate AAMA Voluntary Guide Specification shown (Select from below).

Designation			Description			Standard 				Color

AAM10C21A41			Clear Class I 			AAMA 611				Clear

Eco-friendly etch

AAM10C21A44			Electrolytically			AAMA 611				Champagne, Light Bronze, Medium Bronze

Deposited Class I								Dark Bronze, Extra Dark Bronze, Black					Eco-friendly etch

Exterior Paint			70% PVDF				AAMA 2605				____________ (As selected by Architect)

Suitable for INTERIOR or EXTERIOR finishes

[NOTE: For detailed specifications of other surface treatments and finishes available, as well as sustainable finishing process specification upgrades contact Linetec or Wausau Window and Wall Systems. Color selection is recommended, for the most competitive bids.]

PART 3 EXECUTION

3.01 EXAMINATION

- Site Verification of Conditions

  - Verify that building substrates permit installation of windows according to the manufacturer's instructions, approved shop drawings, calculations and contract documents.

  - Do not install windows until unsatisfactory conditions are corrected.

3.02 INSTALLATION

- Erection of Aluminum Windows

  - Install windows with skilled workers in accordance with approved shop drawings, installation instructions, specifications, and the AAMA Commercial Window and Door Installation Manual.

  - Windows must be installed plumb, square and level for proper weathering and operation.

  - Aluminum that is not organically coated shall be insulated from direct contact with steel, masonry, concrete or other dissimilar metals by bituminous paint, rust-inhibiting primer, non-conductive shims or other suitable insulating material.

[DISCLAIMER:  Wausau Window and Wall Systems takes no responsibility for product selection or application, including, but not limited to, compliance with building codes, safety codes, laws, merchantability or fitness for a particular purpose; and further disclaims all liability for the use, in whole or in part, of these Guide Specifications in preparation of project specifications and/or other documents.  Guide Specifications are subject to change at any time, without notice, and at Wausau’s sole discretion.]

©2014 Apogee Wausau Group, Inc.