Guide Specification - SECTION 08 51 13  ALUMINUM WINDOWS

WAUSAU 4000i and 4000i-DT PSYCHIATRIC SERIES Fixed and In-Swing Casement

[NOTE: Instructional and advisory language in grey italic font.]

PART 1 GENERAL

  - SUMMARY

- Section Includes:

  - All exterior Architectural Performance Class (AW) psychiatric windows furnished and installed as shown on drawings, specified in this section and designated in AAMA/WDMA/CSA 101/I.S.2/A440-08.

  - All labor, materials, tools, equipment and services needed to furnish and install AW Class windows.

  - Components furnished with installed windows.

  - Installation accessories furnished and installed.

  - REFERENCES

- Refer to AAMA/WDMA/CSA 101/I.S.2/A440-08 for a complete list of references and industry standards.

1.03 SYSTEM DESCRIPTION AND PERFORMANCE REQUIREMENTS

A. 	 Design Wind Loads - Allowable Stress Design (ASD)

  - The design wind pressure for the project will be:  (Specify)

    - ___ psf positive and negative; ___ psf negative at corner zones

    - Per wind pressure diagram, (or)

    - Per local building codes

[NOTE: Determination of Design Load(s) is the sole responsibility of the building's Engineer of Record, considering Code interpretation issues and/or prescriptive requirements not included in Contract Documents.  WAUSAU is not responsible for determining Design Loads and strongly recommends that ASD Design Loads (in psf or Pa) specific to all relevant areas of the building be provided by the Specifier.]

  - All structural components, including meeting rails, mullions and anchors shall be designed accordingly, complying with deflection and stress requirements of Paragraph 1.03.B.

- Air, Water and Structural Performance Requirements

  - When tested in accordance with cited test procedures, windows shall meet or exceed the following performance criteria, as well as those indicated in AAMA/WDMA/CSA 101/I.S.2/A440-08 for AW Performance Class windows, Performance Grade 120 (AW120) unless otherwise noted herein.

    - Test units shall not be smaller in either width or height than the “Gateway Test Size” specified in AAMA/WDMA/CSA 101/I.S.2/A440-08 for AW Performance Class.

    - “Downsize” testing to meet Optional Performance Class requirements specified herein shall not be permitted.

    - Test units shall employ manufacturer’s standard sealing, lock spacing and anchorage.

  - Air Test Performance Requirements

    - Air infiltration maximum 0.1 cfm per square foot at 6.24 psf pressure differential when tested in accord with ASTM E283.

  - Water Test Performance Requirements

    - No uncontrolled water leakage at 15.00 psf static pressure differential, with water application rate of 5 gallons/hr/sq ft when tested in accord with both ASTM E331 and ASTM E547.

  - Structural Test Performance Requirements

    - Uniform Load Deflection Test

      - No deflection of any unsupported span L of test unit (framing rails, muntins, mullions, etc.) in excess of L/175 at both a positive and negative load of 120 psf (design test pressure) when tested in accord with ASTM E330.

    - Uniform Load Structural Test

      - Unit to be tested at 1.5 x design test pressure, both positive and negative, acting normal to plane of wall in accord with ASTM E330.

      - No glass breakage; permanent damage to fasteners, hardware parts, or anchors; damage to make windows inoperable; or permanent deformation of any main frame or ventilator member in excess of 0.2% of its clear span.

  - Simulated Human Impact Tests (4000i-DT only - Specifier to complete in consultation with medical and security staff.)

    - Conduct tests in general accordance with AAMA 501.8, to simulate a purposeful shoulder impact from the interior. Test units shall be representative of windows on the project in details of frame connections, glazing, and anchorage.  (Refer to Paragraph 1.04.D below for structural analysis requirements for connections and anchorage.)

    - Test units shall be representative of the largest unit on the project (both width and height), or 4’-0” x 6’-0”, whichever is greater.

[NOTE: The largest test specimen is not necessarily the “worst case” for all components of a window system. Paths for energy absorption will vary considerably depending on factors such as size, configuration, aspect ratio, hardware location, anchor rigidity and substrate. A thorough engineering analysis is recommended before selecting specimens to be tested.]

    - Meeting rails and mullions to be used on the project shall be incorporated in test units, and similarly tested at maximum and minimum unsupported span.

    - Interior of each test unit shall be impacted with a heavy shot bag swung from a vertical height sufficient to generate _____ ft-lb of impact, directed at center-of-glass, corner, hinge, midpoint between locks, and lower jamb locking point.  Center-of-glass impact shall be repeated if any plies break upon impact.

    - At the conclusion of impact testing, the window shall remain intact as a barrier to egress, and meet the performance requirements of AAMA 501.8.

Representative Simulated Human Impact Test Results (for information only)

| Test Report | Maximum Unit Size Tested | Window Type | Interior Glazing Material | Human Impact Energy (ft-lbs) |
| --- | --- | --- | --- | --- |
|  | Width (ft-in) | Height (ft-in) |  |  |  |
| QCT 13-3015.01 | 4’-0” | 6’-0” | Inswing casement or fixed | 1/2" coated polycarbonate | 2000 |
| QCT 13-3013.02 | 6’-0” | 7’-0” | Fixed | 7/16” tempered laminated glass | 2000 |

[NOTE: Impact performance is dependent on unit size, infill, glazing materials and methods, locking, anchorage and test condition variables.  Similarly, appropriate minimum requirements depend on application, occupancy, level of supervision and other project-specific parameters. The Guide Specification language above is intended to provide a general framework for the Design Team to develop an appropriate test regimen. Special consideration should be given to pass/fail criteria. Simulation of physical attack with objects likely to be accessible to occupants may also be advisable. Contact WAUSAU’s Structural Engineering Department for project-specific design input, and refer to the general disclaimer at the conclusion of this Guide Specification for limitations and qualifications.]

- Life Cycle Testing

  - When tested in accordance with AAMA 910, there is to be no damage to fasteners, hardware parts, support arms, activating mechanisms or any other damage that would cause the window to be inoperable at the conclusion of testing.

    - Air infiltration and water resistance tests shall meet the primary performance requirements specified after completion of cycling.

- Condensation Resistance and Thermal Transmittance Performance Requirements

(Wausau recommends specifying U-Factor and SHGC requirements by citing the values used in the default, prescriptive or performance compliance path option employed during permitting. Coordinate with 08 80 00 Glazing.)

  - Perform thermal tests in accordance with NFRC 102 and/or AAMA 1503, or provide finite element computer thermal modeling and calculations per NFRC 100, NFRC 705 or AAMA 507, using DOE/LBL THERM, WINDOW, and/or CMAST software.

    - Thermal Transmittance (U-Factor) for the overall window area shall be less than or equal to _____ BTU/hr-ft2-(F.

    - Solar Heat Gain Coefficient (SHGC) for the overall window area shall not exceed ____.

    - Condensation Resistance Factor (CRF) requirements:  CRF minimum ___ (Frame) and CRF minimum ___ (Glass).

(Visit www.aamanet.org to access the AAMA online CRF Selection Tool. CRF varies with configuration, frame depth, and glass type.  Contact WAUSAU for CRF test data on specific frame-glass combinations in this product family not provided in the table below.)

| Thermal Performance Summary | NFRC U-Factor BTU/hr-ft2-(F | SHGC Range (est.) | AAMA U-Factor BTU/hr-ft2-(F | CRF |
| --- | --- | --- | --- | --- |
|  | Tested | Modeled Range |  | Tested |  |
| 4000i-DT Psychiatric Fixed Window (Triple Glazed) | 0.34 | Not applicable | 0.28 to 0.33 (Per ASHRAE Handbook of Fundamentals) | 0.34 | 57 Frame 81 Glass |
| 4000i-DT Psychiatric Casement Window (Triple Glazed) | 0.39 | Not applicable |  | 0.40 | 60 Frame 81 Glass |
| Unless noted, tested performance data listed is based on 1 “insulating glass exterior (1/4” Viracon VE1-2M with Low-E coating on surface #2, ½” argon fill, stainless spacer, and ¼” clear glass interior), vented air space, and clear ½” polycarbonate interior. NFRC modeling protocols do not yet apply to all dual- or triple-glazed products with between-glass blinds. |

[DISCLAIMER:  Condensation on interior surfaces of installed windows may be affected by many variables, including, but not limited to, component thermal performance, thermal mass of surrounding materials, interior trim coverage and air flow conditions, weather and mechanical system design.  Since many of these variables are outside of our control, WAUSAU makes no representations or warranties against the formation of condensation. Testing is conducted on pre-defined configurations under controlled and steady-state laboratory conditions, as specified above.]

- Acoustic Performance Requirements

  - Perform acoustical tests in accordance with ASTM E90 and ASTM E1425 on the glass type(s) specified in 08 80 00, rigidly supported in aluminum framing of the same product type.

  - “Glass-only” test results shall not be acceptable.

  - Sound Transmission Class (STC) shall not be less than ___. (Specify STC 47 for triple glazing. Coordinate with 08 80 00 Glass and Glazing.)

  - Outdoor-Indoor Transmission Class (OITC) shall not be less than  ____. (Specify OITC 33 for triple glazing. Coordinate with 08 80 00 Glass and Glazing.)

- Sustainable Design Requirements

  - The products provided under this section may affect LEED® certification for the project.  Provide documentation in accordance with USGBC’s “LEED® for New Construction and Major Renovation,” verifying that the components, processes and/or assemblies specified herein conform to the following requirements.  (Select only those Credits needed for the level of certification sought. Modify criteria as necessary for other LEED® programs or versions applicable to specific projects.)

    - EA  Optimize Energy Performance

      - Area-weighted overall U-Factor not to exceed that specified in 1.03.

      - Area-weighted center-of-glass or overall SHGC less than or equal to that specified in 1.03.

    - EA  On-Site Renewable Energy

      - Design framing to accept façade-integrated PV modules and associated NEC-compliant wiring where shown on drawings.

      - Obtain UL 1703 listing for laminate support.

    - MR  Recycled Content

      - Provide window assemblies (aluminum framing, glass and other components) containing no less than ___% (Specify up to 15%) combined recycled content by assembly weight.

      - Combined content to be calculated as post-consumer plus one-half pre-consumer recycled content by weight.

      - Report pre- and post-consumer recycled content separately.

      - All recycled secondary aluminum billet must meet Aluminum Association content requirements for the alloy used.

[NOTE: Secondary aluminum billet contains a high percentage of pre-consumer recycled content, however, glass comprises the majority of the weight of a glazed window assembly.]

    - EQ  Low-Emitting Materials – Adhesives and Sealants

      - All interior primers, structural glazing adhesives and metal-to-metal sealants used on site must meet applicable South Coast Air Quality Management District (SCAQMD) Rule #1168 VOC limits.

    - EQ  Thermal Comfort- Design

      - Provide thermal barrier framing and triple glazing as specified herein and in 08 80 00 Glass and Glazing.

    - EQ  Daylight and Views

      - Area-weighted overall VT not less than 0.____ (Specify – Coordinate with 08 80 00 Glazing) per NFRC 200.

      - Window sizes and configurations as shown on drawings.

  - SUBMITTALS

- General Requirements

  - Provide all submittals in a timely manner to meet the required construction completion schedule.

- Shop Drawings

  - Shop drawings must be prepared wholly by the window manufacturer, or a qualified engineering services firm under the guidance of the manufacturer.  Shop drawings for pre-engineered configurations may be prepared by upon written manufacturer consent.

  - Provide design details along with bid proposals to define system aesthetic and functional characteristics.

  - Provide up to three photocopied sets of shop drawings, including half size details of all necessary conditions.

- Samples

  - Components:  Submit samples of anchors, fasteners, hardware, assembled corner sections and other materials and components as requested by Architect.

  - Finish:  Submit color samples for Architect's approval as requested.

- Test Reports and Calculations

  - Submit certified independent laboratory test reports verifying compliance with all test requirements of 1.03.

  - Submit structural calculations indicating adequacy of all materials furnished under this section, to meet the human impact, uniform and structural load requirements as specified in 1.03.

  - QUALITY ASSURANCE

- Qualifications:  Upon request, the window manufacturer shall provide written consent for the installation subcontractor to install window products to be used on this project.

- In-Plant Testing:  Conduct detailed quality audits and ASTM E331 static water infiltration testing on a minimum of 4% of factory-glazed windows prior to shipping, subject to reasonable unit size restrictions.

  - Each tested unit shall be identified with a removable sticker on the inside glass face.

  - Provide detailed documentation of in-plant testing upon request.

  - DELIVERY, STORAGE AND HANDLING

- Packing, Shipping, Handling and Unloading

  - Materials will be packed, loaded, shipped, unloaded, stored and protected in accordance with AAMA CW-10.

  - WARRANTY

- Aluminum Window Warranty

  - Products:  Submit a written warranty, executed by the window manufacturer, for a period of ___ (up to 10) years from the date of manufacture, against defective materials or workmanship, including substantial non-compliance with applicable specification requirements and industry standards, which result in premature failure of the windows, finish, factory-glazed glass, or parts, outside of normal wear.

[NOTE: Refer to the WAUSAU Standard Limited Warranty for detailed exclusions, qualifications and limitations. Screens and balances are warranted for one year.]

  - In the event that windows or components are found defective, manufacturer will repair or provide replacement material without charge at manufacturer’s option.

  - Warranty for all components must be direct from the manufacturer (non pass-through) and non pro-rated for the entire term.  Warranty must be assignable to the non-residential owner, and transferable to subsequent owners through its length.

PART 2 PRODUCTS

2.01 MANUFACTURERS

- Acceptable Manufacturer

  - Drawings and specification are based on:

    - Wausau Window and Wall Systems – (Select one) [4000i-DT Series Psychiatric]  [4000i Series]  Fixed and In-Swing Casement Windows.

      - Base bid will be Wausau Window and Wall Systems

  - Substitutions

    - Other manufacturers’ products that meet or exceed specified design requirements may be considered.  Submit the following information with request for substitutions at least ten (10) working days prior to bid date.

      - Test reports specified in 1.03.

      - Full proposal details and samples specified in 1.04.

      - Copy of manufacturer's warranty specified in 1.07.

      - Proof of at least 10 years experience in the design and fabrication of psychiatric windows.

      - Other information as requested for evaluation

  - Substitute products not pre-approved by the Architect via addenda will not be considered.

  - Clear preference will be given to products produced in LEED®-certified manufacturing facilities.

2.02 MATERIALS

- Aluminum Framing Members

  - Extruded aluminum billet, 6063-T5 or T6 alloy for primary non-radius components; 6063-T5 or T6, 6005-T5, 6105-T5 or 6061-T6 for anchor components; all meeting the requirements of ASTM B221.

  - Aluminum sheet alloy 5005-H32 (for anodic finishing), or alloy 3003-H14 (for painted or unfinished sheet) meeting the requirements of ASTM B209.

  - Principal window frame and sash ventilator members will be a minimum 0.125" in thickness at glazing legs, hardware mounting webs and section flanges.

  - (4000i-DT only) Extruded aluminum security glazing stops will be a minimum 0.125” in thickness.

  - Extruded or formed trim components will be a minimum 0.060" in thickness.

  - Perimeter frame depth 4" minimum.

  - Sash ventilator and fixed lite access panel sections must be tubular and overlap framing members.

    - Vented areas shall be indistinguishable in sightline from fixed areas from the exterior, with vents in the closed position.

    - Sash ventilator joinery shall not be exposed to the exterior with vents in the closed position.

  - Exterior sightlines at perimeter framing members will not exceed 3 ½ " unless detailed otherwise on architectural drawings.

2.03 COMPONENTS

- Hardware (Select from options as noted)

  - All steel components including attachment fasteners to be 300 Series stainless steel except as noted.

  - Extruded aluminum components 6063-T5 or -T6.

  - Locking handles, bases and strikes to be aluminum, die cast, white bronze or stainless steel in manufacturer’s standard surface finish.

  - Thermo-plastic or thermo-set plastic caps, housings and other components to be injection-molded nylon, extruded PVC, or other suitable compound.

  - Hardware to be custodial- or supervisory-operated and include: (Select from appropriate options listed in the WAUSAU Hardware Selection Guide: concealed extruded aluminum butt hinges, tamper-resistant custodial locks, keyed GEM® cylinder locks, concealed friction adjusters, concealed limited opening devices, safety escutcheon plates.)

- Sealants

  - All sealants shall comply with applicable provisions of AAMA 800 and/or Federal Specifications FS-TT-001 and 002 Series.

  - Frame joinery sealants shall be suitable for application specified and as tested and approved by window manufacturer.

- Glass and Security Glazing Infill Material (Specifier to complete in consultation with medical, security and maintenance staff.)

  - Provide in accordance with Section 08 80 00.

  - Sealed insulated glass shall be tested and certified in accord with ASTM E2190.

  - (4000i-DT only) Interior security glazing infill material to be _________________ in accordance with Section 08 80 00.

[NOTE: If patients have unsupervised access to the building exterior, special consideration should be given to exterior glass selection.]

- Glazing

  - Provide in general accordance with Section 08 80 00.

  - Glazing method shall be in general accordance with the GANA Glazing Manual for specified glass type, or as approved by the glass fabricator.

  - (4000i-DT only) Glazing stops retaining security glazing shall be attached at 12” on center using ¼”-20 stainless steel machine screws.

  - (4000i-DT only) Glazing materials at the interior must be rendered tamper-resistant by a continuous extruded hood projection or other tested and approved method.

  - (4000i-DT only) Provide minimum glazing “bite” as recommended by the security glazing infill fabricator and tested per 1.03.

  - Provide windows factory-glazed wherever practical.

- Glazing Materials

  - Setting Blocks/Edge Blocking:  Provide in sizes and locations recommended by GANA Glazing Manual. Setting blocks used in conjunction with soft-coat low-e glass shall be silicone.

  - Back-bedding tapes, expanded cellular glazing tapes, toe beads, heel beads and cap beads shall meet the requirements of applicable specifications cited in AAMA 800.

  - Glazing gaskets shall be non-shrinking, weather-resistant, and compatible with all materials in contact.

  - Structural silicone sealant where used shall meet the requirements of ASTM C1184.

  - Spacer tape in continuous contact with structural silicone shall be tested for compatibility and approved by the sealant manufacturer for the intended application.

  - Gaskets in continuous contact with structural silicone shall be extruded silicone or compatible material.

- Steel Components

  - Provide steel reinforcements as necessary to meet the performance requirements of 1.03.

  - Concealed steel anchors and reinforcing shall be factory painted after fabrication with TGIC powder coating, or rust-inhibitive primer complying with Federal Specification TT-P-645B.

- Panning: (Optional)

  - Provide extruded aluminum panning to receive replacement windows as shown on architectural drawings.

  - Panning shall be pre-assembled and all joinery back sealed prior to installation.

  - Finish to match window frames.

- Receptors:  (Optional)

  - Provide extruded aluminum receptors to receive windows, as shown on architectural drawings.

  - Finish to match window frames.

  - (4000i-DT only) If provided, receptors must be tested to the performance requirements of 1.03.B.5 and structural calculations provided per 1.04.D.2.

- Insect Screens: (Optional)

  - Tubular extruded aluminum frames shall meet the requirements of ANSI/SMA 1004.

  - Screen frame finish to match window frames.

  - Aluminum cloth shall comply with GSA-FS-RR-W-365 and USDC-CS-138 with 18 x 16 mesh.

  - Cloth mesh color shall be ________________. (Specify bright mesh or charcoal mesh)

- Dual or Triple Glazed Access Panel:

  - Hinged access panel shall be constructed with mitered corners, mechanically staked over a solid aluminum corner block leaving hairline joinery.

  - Provide a hook latch for custodial operation.

  - Finish to match window frames.

- Integral Venetian Blinds: (Optional)

  - 5/8" or 1" (Select one)  wide aluminum slat blinds. Blind color shall be _____________.  (Specify from standard color chart.)

  - Blind to be integrally mounted between the dual or triple glazing.

  - Removable tilt-control knob will be located on the interior face and incorporate a "slip clutch" feature.

  - Raise and lower pull cords will be located between glass for access only when glazed access panel is opened.

2.04 FABRICATION

- General:

  - Finish, fabricate and shop assemble frame and sash ventilator members into complete windows under the responsibility of one manufacturer.

  - No bolts, screws or fastenings shall impair independent frame movement, or bridge the thermal barrier, unless such bridging was also present in thermal test units and thermal models.

  - Fabricate to allow for thermal movement of materials when subjected to a temperature differential from -30 (F to +180 (F.

- Frames:

  - Miter each perimeter frame corner, then mechanically stake over a solid extruded aluminum corner block or weld; then seal weather tight.

  - Cope and mechanically fasten each intermediate meeting rail; then seal weather tight.

  - Make provisions for continuity of frame joinery seals at extrusion webs.

- Main Sash and Access Sash Ventilators

  - Miter all corners and mechanically stake over a solid extruded aluminum corner block, set and sealed in epoxy, leaving hairline joinery.

- Glass Drainage: (field glazed units only)

  - Provision shall be made to insure that water will not accumulate and remain in contact with the perimeter area of sealed insulated glass.

- Hardware: (Select from options as noted.)

  - Concealed Hinges at Sash Ventilator and Fixed Lite Access Panels

    - Provide two concealed extruded aluminum “walk-around” butt hinges with stainless steel pins. Provide three hinges on in-swing casement units over 4’-0” in height.

  - Locks

    - Die cast or stainless steel cam locks, strikes and/or keepers for custodial or supervisory operation shall secure sash in closed position. (Refer to WAUSAU Hardware Selection Guide)

    - (4000i-DT only) Provide tamper-resistant locks for ventilators at maximum 48" spacing. Keys shall not be removable in the unlocked position.

  - Provide a supplemental keyed GEM® lock for interior sash ventilators and access panels. (Optional)

  - Friction Adjuster

    - Provide concealed device with adjustable friction shoe to arrest sash opening before contact with adjacent materials occurs.

  - Limited Opening Device

    - Provide concealed device to limit initial sash operation to 4". Operation past this point to be by use of a tool or removable key.  (Optional)

  - Dual or Triple Glazed Access Panel at Sash Ventilators

    - Access panel to have a custodial hook latch.

- Dual or Triple Glazed Access Panel (Select)

  - Hinged access panel  will be constructed with mitered corners, mechanically staked over a solid aluminum corner block leaving hairline joinery.

- Thermal Break Construction:

  - Continuous extruded 6/6 polyamide nylon with 25% glass fiber reinforcing, mechanically crimped into cross-knurled cavities.

  - Minimum thermal separation 3/8".

  - Quality assurance records must be maintained and available as requested.

- Weather-stripping:

  - Bulb- or fin-type neoprene, EPDM, dual-durometer PVC, polypropylene, TPE, or other suitable material as tested and approved by the window manufacturer.

  - Miter, crowd, stake or join at corners. Provide drainage to exterior as necessary.

  - Provide weather-strip at access panels for minimum thermal separation of ¼ “.

  - Weather-stripping shall provide an effective pressure-equalization seal at the interior face of the sash ventilator..

2.05 FINISHES

- Finish of Aluminum Components

  - Finish of all exposed areas of aluminum windows and components shall be done in accord with the appropriate AAMA Voluntary Guide Specification shown (Select from below).

Designation			Description			Standard 				Color

AAM10C21A41			Clear Class I 			AAMA 611				Clear

Eco-friendly etch

AAM10C21A44			Electrolytically			AAMA 611				Champagne, Light Bronze, Medium Bronze

Deposited Class I								Dark Bronze, Extra Dark Bronze, Black, or				Eco-friendly etch								Copper Anodize

Interior Paint			50% PVDF,				AAMA 2603				____________ (As selected by Architect)

Enamel, Acrylic									Suitable for INTERIOR finishes

or Polyester

Exterior Paint			70% PVDF				AAMA 2605				____________ (As selected by Architect)

Suitable for INTERIOR or EXTERIOR finishes

[NOTE: For detailed specifications of other surface treatments and finishes available, as well as sustainable finishing process specification upgrades contact Linetec or Wausau Window and Wall Systems. Color selection is recommended, for the most competitive bids.]

PART 3 EXECUTION

3.01 EXAMINATION

- Site Verification of Conditions

  - Verify that building substrates permit installation of windows according to the manufacturer's instructions, approved shop drawings, calculations and contract documents.

  - Do not install windows until unsatisfactory conditions are corrected.

3.02 INSTALLATION

- Erection of Aluminum Windows

  - Install all windows with skilled workers in accordance with approved shop drawings, installation instructions, specifications, and the AAMA Commercial Window and Door Installation Manual.

[NOTE: Windows in psychiatric and behavioral care facilities are often required to be designed to withstand significant interior human impacts. For new construction and renovations, the installer shall allow for secure anchorage into adequate substrates.  Adequate substrates may include, but are not limited to, steel liners, reinforced steel studs, continuous structural grade lumber, grout-filled concrete masonry units, or structural concrete. Based on the adequate substrate surrounds, Wausau will provide a fastener recommendation for specified interior human impacts. The specifier is encouraged to identify any special interior sealants, trim, or other appurtenances related to occupant safety and security in the appropriate specification Section(s).]

  - Windows must be installed, and remain, plumb, square and level, to one-half of the unit shimming tolerances cited in the AAMA Commercial Window and Door Installation Manual, for proper weathering and operation. Installer to make necessary final hardware adjustments on site.

  - Aluminum that is not organically coated shall be insulated from direct contact with steel, masonry, concrete or other dissimilar metals by bituminous paint, rust-inhibiting primer, non-conductive shims or other suitable insulating material.

[DISCLAIMER:  Wausau Window and Wall Systems takes no responsibility for product selection or application, including, but not limited to, compliance with building codes, safety codes, laws, merchantability or fitness for a particular purpose; and further disclaims all liability for the use, in whole or in part, of these Guide Specifications in preparation of project specifications and/or other documents.  Guide Specifications are subject to change at any time, without notice, and at Wausau’s sole discretion.]

©2014 Apogee Wausau Group, Inc.